ILLINOIS TOLLWAY									AC-220

CHECKLIST FOR

PILING

While its use is not required, this checklist has been prepared to provide for the field inspector a summary of easy-to-read step-by-step requirements for the installation and inspection of foundation piling (Section 512).  The following questions are based on information found in Tollway Supplemental Specifications, Tollway Standards, IDOT Standard Specifications, IDOT Highway Standards, IDOT Constructions Manual and current policy memorandums and letters.

Have you checked the contract Special Provisions, Supplemental Specifications and plans to see if any modifications have been made to the requirements listed herein?	____

# 1.	PLAN AND SPECIFICATION REVIEW

Prior to starting work on an item, have you checked the contract Special Provisions and plans to see if any changes or modifications have been made to the Standard and Supplemental Specifications?	____

On bridge construction and reconstruction contracts have you checked the proposed or existing span lengths prior to starting work?  (This is the responsibility of the Contractor.) 	____

On bridge construction and reconstruction contracts have you checked the existing or proposed vertical or horizontal clearances? 	____

Prior to the start of construction, have you checked the plan elevations of the bottom of footings, intermediate substructure components and bearing seat elevations of abutments and piers to ensure they correspond to the appropriate top of deck elevations and dimensions shown on the superstructure plans? 	____

Has the structure been surveyed to establish the baseline of the structure, bearing lines of piers and backs of abutments? Has an independent check of your calculations and layout been performed before the work starts?	____

# 2.	DETERMINE HAMMER ENERGY REQUIREMENTS

Have you the Contractor provided the Engineers with the data and necessary correlation charts for determining the energy “E” developed by the hammer per blow for the pile hammer proposed for driving piles?	____

If the contract indicates a Wave Equation analysis will be used to drive the project piles, have you submitted your analysis to Tollway for their review and approval?	____

Does the hammer meet the following energy requirements:	____

- Minimum Hammer Energy:

E> 0.082 x [RN +100]2  (English)

- Maximum Hammer Energy:

E< 0.193 x [RN +100]2  (English)

Where: 
RN = Nominal Required bearing in kips
E =   Energy developed by the hammer per blow in ft-lbs.

# Additional Hammer Requirements (by Hammer type):

Air/Steam Hammers

Is the total weight of the striking parts least 1.4 tons and not less than 1/3 the weight of the Pile and drive cap? 	____

Diesel Hammers

Is the hammers either equipped with a device to measure ram impact velocity or speed of operation (with the necessary correlation charts) or designed such that the stroke height can be directly observed? 	____

If the hammer is closed-end (double acting) is it equipped with a bounce chamber pressure gauge that is easily readable? 	____

Have you the Contractor provided the correlation chart and hammer data to determine the energy developed by the hammer with each blow? 	____

Drop Hammers

Shall not be used for driving: 
Precast and Precast Prestressed Concrete Piles.
Piles with a Nominal Required Bearing (RN) > 120 kips

Is the hammer ram weight (mass) at least 1 ton? 	____

Is the Ram weight at least equal to the combined weight of the pile and drive cap? 	____

Does the fall of the ram not exceed 15 ft.? 	____

Hydraulic Hammers:
Is the hammer equipped with an energy reading device? 	____

# 3.	DETERMINE THE NUMBER OF REQUIRED HAMMER BLOWS

Have you determined minimum number of blows/inch “Nb”, to obtain a Nominal Driven Bearing (RNDB) of the pile equal to or exceeding the Nominal Required Bearing (RN) shown on the plans?	____

Nb=10RN+1001.75E10 (English)

Where:

RN  is the Nominal Required Bearing in kips

E is the Energy developed by the hammer per Blow in Ft-lbs

Nb is the number of hammer blows per inch of pile penetration

# 4.	TEST PILES (Form A-12)

When test piles are specified, are the following requirements being met:

a.	Location:  Are the test piles being located at the substructure foundation designated in the plans?	____

Within the designated substructure foundation, are you locating the test pile as far as possible away from the nearest soil boring? 	____

Test piles driven in a production location cut off as production piles?	____

Are steel test piles driven in a production location painted when painting is specified for the production steel piles?	____

Are test piles not driven as production piles cutoff or pulled as directed by the Engineer? (512.15)	____

b.	Driving Elevation:  Keep the excavation at the test pile location completed to an elevation no more than 2 ft above the plan bottom of footing elevation?  (512.15)	____

c.	Pile Material:  Is the test pile the same material and size as specified for the production piles? (512.15)	____

If pile shoes are specified for the production piles, is the test pile driven with the required pile shoe?	____

d.	Length:  Is the test pile at least 10 ft longer than the estimated length of the production piles shown on the plans? (512.15)	____

e.	Hammer:  Is the hammer proposed to drive the test pile the same hammer that will be used to drive the production pile? (512.15)	____

f.	Bearing:  Is the test pile being driven to a Nominal Driven Bearing (RNDB) =1.1 x Nominal Required Bearing (RN) shown on the plans? (512.15)	____

Is the Nominal Driven Bearing (RNDB) being determined by the appropriate formula (modified Gates or Wave)? (512.14)	____

Is the Nominal Driven Bearing (RNDB) > the Nominal Required Bearing (RN) indicated on the plans? (512.11(a))	____

Does the pile penetrate to at least the minimum pile tip elevation specified, or if none is specified, at least 10 ft below the bottom of footing elevation or 10 ft below undisturbed earth?  (512.11(b))	____

g.	Records:  Are the test piles marked off in 1 ft increments and the blows per 1 ft foot recorded on the Test Pile Driving Record, for each 1 ft of test pile driven? (512.15)	____

h.	Length Determination:  Are the lengths of the production piles being determined from the test pile data?	____

Have you been furnished a written itemized list of pile lengths to be ordered? (512.16)	____

Is a copy of this list being retained in the contract documentation files?	____

# 5.	STORAGE AND HANDLING

a.	Timber Piles:  Are the treated timber piles stored at the site of the work in accordance with the requirements of 1007.13 and handled in accordance with Articles 507.05 and 1007.13? (512.08(a))	____

Are the piles being stored off the ground on solid timbers of size and so arranged as to support treated materials without producing noticeable distortion and not subjected to standing water? (1007.13/AWPA Std M4)	____

Are the piles being handled with rope slings and in accordance with Article 507.05(a) and 1007.13?  (512.08(a))	____

b.	Precast Concrete Piles:  Are precast and precast prestressed concrete piles being lifted and stored at the bridle points shown on the plans?  512.08(b)	____

c.	Steel piles:  Are steel H-piles being supported on skids or other supports sufficiently spaced to keep the piles clean and free from injury? (512.08)(c) / 505.08(c))	____

d.	Metal Shell Piles.  Are metal shell piles being stored off the ground and in a manner to prevent dirt, water or other foreign material from entering the shell? (512.08(d))	____

Are metal shell piles being stored on sufficient wood cribbing to prevent bending, distortion or other damage to the shell? (512.08(d))	____

# 6.	PREPARATION FOR DRIVING

a.	Prior to the start of driving piling, has the footing been excavated to grade? (512.09)	____

b.	Have cross sections been taken to determine pay quantities for structure excavation?	____

c.	Have the pile locations been staked and checked?	____

d.	Has the entire length of all precast concrete piles been kept saturated at least six hours prior to driving? (512.09(b))	____

e.	If pre-coring of the embankment is specified on the plans, has the contractor pre-cored to the required depth and diameter shown on the plans?	____

# 7.	PILING DOCUMENTATION

Are you preparing a field book or other record so that a permanent record can be made of the following:  	____

a.	A numbered diagram of the location of piles in each substructure location.	____

b.	The authorized length to be furnished as per the written itemized list.	____

c.	The actual measured length of piling delivered.	____

d.	The length of cutoff (top of pile elevation -- cutoff elevation)	____

e.	The length driven (length of pile furnished-- cutoff length)	____

f.	The hammer blows per inch “Nb”, Hammer energy “E” imparted and corresponding calculated Nominal Driven Bearing (RNDB) at the final bearing.	____

# 8.	MATERIAL INSPECTION

a.	Have you inspected all piling to see if they have been approved prior to shipment?  	____

b.	Are you inspecting piling delivered for possible damage in transit?	____

c.	If pile shoes are specified, do they meet the requirements 
of (512.05(c) & 1006.05(e))?	____

# 9.	EQUIPMENT

a.	Drive Head:  Are the heads of all piles being protected with a suitable driving head? (512.10(b))	____

b.	Pile Cushion:  Are the heads of all Timber, Precast Concrete and Precast Prestressed Concrete piles being protected by a Pile cushion? 	____

Is the thickness of the Pile head cushion at least 3 inches? 	____

Are you required to replace the cushion when it compresses to less than 60% of its original thickness or begins to burn? 	____

c.	Hammer Cushion:  Are you inspecting the Hammer cushion, when one is required by the manufacturer prior to driving and after each 50 hours of operation? 	____

Is the hammer cushion being replaced when it is reduced to less than 75% of its original thickness?	____

d.	Leads:  Is the pile and hammer being held in accurate alignment with pile leads which are blocked in position on the pile? (512.10(d))	____

If swinging leads are used, are they firmly toed into the ground prior to starting the pile driving operation?	____

e.	Followers:  If you request permission to use a follower to drive pile, has the CM agreed to its use in writing? 	____

Is the first pile in every group of ten being driven without a follower and the data from that pile used to determine the average Nominal Driven Bearing (RNDB) of the other piles in the group? 	____

f.	Jets:  If jets are proposed, have you approved their use? 	____

Following termination of use of jets in a substructure unit, are you further driving each pile in that unit to ensure the Nominal Driven Bearing (RNDB) is equal to or greater than the Nominal Required Bearing (RN)? 	____

# 10.	TOLERANCES IN DRIVING

a.	Are foundation piles being driven with a variation from the vertical or required batter alignment of not more than 1/4 in/ft. (512.12)	____

b.	Are piles driven such that no visible portion of the pile is more than 6 inches out of plan position, when such alignment does not require a design modification and forcing in to this position does not result in injury to the pile? (512.12)	____

# 11.	PENETRATION REQUIREMENTS

a.	Are you observing the hammer blow per inch to ensure the piling is driven to a Nominal Driven Bearing (RNDB) equal to or larger than the Nominal Required Bearing (RN) shown on the plans?	____

b.	If the pile has not achieved Nominal Required Bearing (RN) at the full furnished length, but has achieved at least 85% of RN, are you allowing the pile to set for 24 hours to achieve soil setup? (512.11)	____

If soil setup is needed for the Nominal Driven Bearing (RNDB) to equal or exceed the Nominal Required Bearing (RN), before setting back on the pile, has the hammer been warmed up by applying at least 20 blows to another pile? 	____

Has Nominal Required Bearing been determined by driving the pile over an additional 3 inch distance? 	____

c.	When a minimum tip elevation is shown on the plans, is the penetration of all foundation piles below the minimum tip elevation?  (512.11) 	____

When a minimum tip elevation is not shown on the plans are the piles being driven to a penetration at least 10 ft below the bottom of footing or into undisturbed earth, whichever is greater?  (512.11)	____

d.	Are you checking that piles in stream beds or on banks of streams, where erosion or scour is expected, (as shown on the scour table shown on the plans) that the pile tip penetrates to the required elevation?	____

# 12.	FIELD SPLICING OF PILES

When it becomes necessary to splice onto a partially driven pile because it has become damaged in driving or because Nominal Required Bearing (RN) shown on the plans has not yet been reached, is the splice being performed in accordance with the plan details and the following?	____

a.	Precast or Precast Prestressed Concrete Piles:
NO splices are allowed in Precast or Precast Prestressed Concrete Piles.	____

If an extension is required, it should be constructed as shown on the plans. (Pile is NOT redriven following constructing the extension) (512.03(c))	____

b.	Metal Shell Piles.

Planned Splice:  Is the Minimum length of each segment at least 
20 ft long? (512.04(a)(1))	____

Unplanned Splice:  Is the minimum length at least 10 ft long? (512.04(a)(2))	____

Is the Splice being accomplished by: 
	(1)  a Complete Joint Penetration (CJP) weld of the entire
		cross-section; or
	(2)  use of a commercial splicer with a Department approved
		commercial splicer welding detail? 	____

Is the welder making the splice qualified by test in accordance with the qualification requirements of the American Welding Society (AWS) Standard Specifications (Certification by independent test laboratory required). (512.07)	____

- Steel “H” Piles.

Planned Splice:  Is the Minimum length of each segment at least 
20 ft long? (512.04(a)(1))	____

Unplanned Splice:  Is the minimum length at least 10 ft long? (512.04(a)(2))	____

Is the splice being accomplished by:
	(1)  a Complete Joint Penetration (CJP) weld of the entire
		cross-section;
	(2)  the Department’s standard steel pile field splices; or
	(3)  use of a commercial splicer with a Department approved
		commercial splicer welding detail? 	____

Is the welder making the splice qualified by test in accordance with the qualification requirements of the American Welding Society (AWS) Standard Specifications (Certification by independent test laboratory required). (512.07)	____

d.	Timber Piles.   Planned splicing of timber pile is NOT allowed.  For an unplanned splice, is the added piece cut flush with and attached to the main pile with the use of at least 4 steel plates or a metal pipe sleeve.  (512.06)	____

# 13.	PILE CUTOFFS

a.	Are you marking each pile at the cutoff elevation so that the Contractor can cut them off square (perpendicular) to the axis of the pile?  (512.13)	____

b.	Once it is determined that the pile cutoffs will not be needed as splices for any of the other production piles, the cutoffs are to be disposed of at no additional expense to the Tollway?  (512.13)	____

# 14.	INSPECTION OF METAL SHELL PILES AFTER DRIVING

a.	Are you inspecting the interior of all driven metal shell piles for bends or other deformations that would impair the strength of the pile with a Contractor-supplied lamp or mirror?  (512.04(c))	____

b.	After you have inspected and approved the metal shell piles, are you temporarily sealing the top of the metal shell piles to prevent the entrance of water or foreign substance? (512.04(c))	____

# 15.	FILLING METAL SHELL PILES WITH CONCRETE

a.	If all piles in a bent, pier or abutment cannot be driven before any concrete is placed in the metal shell piles, is driving of the additional piles within 15 feet being deferred until the concrete in the metal shell piles within this zone is at least 24 hours old?  (512.04(b))	____

b.	If reinforcement is specified on the plans, is the reinforcement rigidly fastened together and lowered into the shell before placing concrete?  Are spacers used to maintain the proper clearance into the top of the piles?  (512.04(D))	____

c.	Just prior to filling metal shell piles with Class SI Concrete, are you inspecting the interior with a mirror or lantern to be sure that all water and foreign substance has been removed?  (512.04(e))	____

d.	When filling the metal shell piles with concrete, is the top 10 feet of concrete being consolidated with internal vibration?  (512.04(e))	____

# 16.	BACKFILLING PRECORED HOLES

Are all pre-cored holes being backfilled with loose, dry sand after the piles are driven?  (512.09(c))	____

# 17.	PILING DIAGRAM

Is a A-13 Form being prepared for each footing for submittal to the job records?  	____

Have you included a diagram numbering the piles driven and indicating their locations and any deviations from plan locations?	____